Sample Specification 2100

- Restrained flange adapters shall be used in lieu of threaded, or welded, flanged spool pieces. Flange adapters shall be made of ductile iron conforming to ASTM A536 and have flange bolt circles that are compatible with ANSI/AWWA C110/A21.10.

- Restraint for the flange adapter shall consist of a plurality of individual actuated gripping wedges to maximize restraint capability. Torque limiting actuating screws shall be used to insure proper initial set of gripping wedges.

- The flange adapter shall be capable of deflection during assembly, or permit lengths of pipe to be field cut, to allow a minimum of 0.6” gap between the end of the pipe and the mating flange without affecting the integrity of the seal.

- For PVC pipe, the flange adapter will have a pressure rating equal to the pipe.

- For ductile iron pipe, the flange adapter shall have a safety factor of 2:1 minimum.

- The flange adapter shall be the SERIES 2100 MEGAFLANGE adapter, as produced by EBAA Iron, Inc., or approved equal.