# Sample Specification

- Expansion joints shall be installed in the locations indicated on the drawings and shall be manufactured of ductile iron conforming to the material requirements of ASTM A536 and ANSI/AWWA C153/A21.53. Foundry certification of material shall be readily available upon request.

- Each expansion joint shall be pressure tested prior to shipment against its own restraint to a minimum of 350 PSI for 4-inch through 12-inch. A minimum 2:1 safety factor, determined from the published pressure rating, shall apply.

- Each expansion joint shall have 8-inches minimum expansion. The expansion fitting shall not expand or exert an axial imparting thrust under internal water pressure. The expansion fitting shall not increase or decrease the internal water volume as the unit expands or contracts.

- All internal surfaces (wetted parts) shall be lined with a minimum of 15 mils of fusion bonded epoxy conforming to the applicable requirements of ANSI/AWWA C213. Sealing gaskets shall be constructed of EPDM. The coating shall meet ANSI/NSF-61.

- Exterior surfaces shall be coated with a minimum of 6 mils of fusion bonded epoxy conforming to the applicable requirements of ANSI/AWWA C116/A21.16.

- Polyethylene sleeves, meeting ANSI/AWWA C105/A21.5, shall be included for direct buried applications.

- Manufacturer’s certification of compliance to the above standards and requirements shall be readily available upon request. The purchaser (or owner) shall reserve the right to inspect the manufacturer’s facility for compliance. All expansion joints shall be The Force Balanced EX-TEND as manufactured by EBAA Iron, Inc. Eastland, TX., U.S.A.

This Sample Specification is available as a Microsoft® Word Document at www.ebaa.com/products/flex.